Refrigeration Plant with

Heat Recovery System

manual for simulation

using WinDali Simulation Interface

Jacob Iløse & Kenneth Tolstrup Kristensen

Department of Mechanical Engineering

Technological University of Denmark

January 2004

Contents

1	Disclaimer	4

2	Getting started	5

3	WinDali Simulation Interface	6

4	Plant	9

5	General compressor settings	12

6	Low, Medium and High stage compressors	13

7	Warm water production	15

8	Cooling demands	21

8.1	Profile Editor	21

8.2	Cooling demands	22

9	Graphs	24

10	Results	25

11	Parameter Analysis	28

11.1	Varying parameters	28

11.2	Online Parameters	31

# Disclaimer

We have done our best to make the program as robust, error free, relevant, and as easy to use as possible. However, we cannot guarantee the program is free from errors. It is practically impossible to build in safe guards preventing the program from being used in ways that were not intended; therefore users are advised to evaluate all results thoroughly before use.

Please do not hesitate to contact us by e-mail if this manual leave questions unanswered or if experiencing problems in using the model.

ktkristensen@get2net.dk

jacob_ilsoe@hotmail.com

# Getting started

This manual is a guide on how to use the model “Refrigeration Plant with Heat Recovery System” in WinDali. The main goals for this manual are depicted below.

- Help the user to get started using the program

- A description of the Simulation Interface in general

- Help to understand the results produced by the model

In the CD-rom open the file “simulation.exe” to start the simulation program. Go to menu “File” and use the “open model...” function.

Figure 1: How to open a model

To perform simulations choose “HeatRecoverySystem.mdl”. You are now ready to start simulating.

# WinDali Simulation Interface

The simulations are conducted in the simulation interface for WinDali. This section describes the interface in general and is based on the WinDali manual.

Commands

In this section the commands available to the user in the Simulation Interface are listed. These commands are used when running a simulation.

Table 1: Commands in File Menu

If a settings file is saved with the same name as the model file and in the same directory (but with extension .set), this file will be loaded by default when the model is opened again. This file holds the settings of the simulation window, such as entered parameters, variables chosen to be plotted etc.

The Plot, Edit, Draw, View and Format menus are explained in the accompanying help file (select the Help|Plot menu), except for the following items in the plot menu:

Table 2: Commands in Plot Menu

Using the commands above it is possible to “personalize” the plot settings. The following commands are used to conduct the actual simulation.

Table 3: Commands used for running simulations

Simulation window

Starting the simulation program you will see a screen with these main features (not all windows will be expanded).

Figure 2: WinDali interface set-up

The items in the figure are:

- Plot Window 1 and 2 are where results are plotted. You can add as many plots as you want. Normally only Plot Window 1 is opened, but you can open number 2 by pressing .

- Curve Window lists the variables you can plot. If both plot 1 and 2 are visible, the first column checkboxes select curves in plot 1 and the second column selects curves in plot 2.

- Message Window, which has two pages:

  - Solver, here messages from the solver are displayed

  - Debug, shows debug messages from the model.

- Data Window, here you can inspect the numerical values of the selected variables. You bring up the data window by pressing .

- Online Parameters, here you can change parameters during simulations, see “11  Parameter”.

The image of the Simulation Interface program will change according to the model loaded. As default the following pages will be shown

- General

- Initial

- Guesses

- Results

- Cases

Refer to the WinDali manual for elaboration of the parameters included in these headings. The only parameter that has immediate interest to the current model is found on page “Results”, which displays the results of the simulations.

After the model “Refrigeration Plant with Heat Recovery System” (HeatRecoverySystem.mdl) is loaded, the following menus are available.

Figure 3: Menus associated to “Refrigeration Plant with Heat Recovery System”

As shown in Figure 3, some extra headings are included in the developed model:

- Plant

- Cooling demands

- Compressor general

- Low stage compressors

- Medium stage compressors

- High stage compressors

- Warm water production

In the next sections, the parameters and settings under each heading will be elaborated on. The default values are chosen to reflect a real refrigeration plant.

# Plant

The “Plant”-menu is shown in the figure below.

Figure 4: Menu for specifying the refrigeration plant

The menu is divided into three parts.

Temperature levels

Here the condensing - and subcooling temperature are set. The evaporating temperature is set separately for up to three cooling stages, the number of which determined by the checkboxes. It should be noted that the cooling has a common condensing temperature. An example of a plant layout having the following configuration is shown on the next page.

Plant configuration:

| Compressors configuration |  | Te | Tc | Economizer |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Screw nr. 1 | -40C | 30C | Yes |  |  |
|  | Screw nr. 1 | -40C | 30C | Yes |  |  |
|  | Screw nr. 1 | -40C | 30C | Yes |  |  |
|  | Reciprocating | -40C | 30C | No |  |  |
|  | Reciprocating | -10C | 30C | No |  |  |
|  | Reciprocating | -10C | 30C | No |  |  |
|  | Reciprocating | 0C | 30C | No |  |  |
|  | Reciprocating | 0C | 30C | No |  |  |

Figure 5: Example of cooling plant with heat recovery system

Economics

Here the prices of electricity and heat are specified.

Evaporative condensers

The number of evaporative condensers is specified. The load is distributed evenly between each condenser. The nominal capacity, nominal power consumption, and wet bulb temperature are also set. The nominal capacity must be specified for 30˚C condensing temperature and 20˚C wet bulb temperature.

# General compressor settings

Even though the model allows performing simulations on a wide range of compressors, there are some specifications which are common to all.

Figure 6: Menu for general compressor settings

Compressor losses

The suction line pressure loss is defined as the ammonia temperature drop (Celsius) from the evaporator to the compressor suction head. This value is common for the low, medium, and high temperature stages.

The discharge line pressure loss is defined as the ammonia temperature drop (Kelvin) from the compressor to the heat exchanger for removal of superheat. This setting is also common for the low, medium and high temperature stages.

Oil inlet temperature

This parameter sets the temperature (degree Celsius) of oil entering the compressors. Changes in this parameter only affect the screw compressors.

Specify compressor RPM limits

This option is for specifying the minimum and maximum speeds (Revolutions Per Minute) at which the compressors can operate using a frequency control. As default the values suggested by the manufacturer are loaded.

By changing these parameters the capacity of the compressors are altered.

# Low, Medium and High stage compressors

In these menus the compressor configurations are specified. Up to a number of four different compressors are possible for each stage.

Figure 7: Specification of low stage compressor configuration

The menus for low, medium, and high stage compressors are alike.

Calculate compressor load curves

This check box indicates whether or not the model should calculate the optimal compressor load conditions before running the simulation. These calculations are always performed before the first simulation. The compressor load conditions should be recalculated after changes in one or more of the following parameters:

- Suction line pressure loss and/or discharge pressure

- Evaporator and/or condenser temperature

- Subcooling

- The compressor configuration is changed in any way (i.e. frequency control included/not included, with or without economizer, increase/decrease in number)

If none of the above parameters change during a series of simulations, there is no need to calculate the optimal compressor load configurations. This cuts a great deal of the computation time.

The required time to calculate the optimal compressor load configurations is primarily dependent on the number of compressors chosen for each temperature level.

Specify compressor

A maximum of four compressors can be specified at each temperature level. A total of 30 York Refrigeration compressors are included, 16 reciprocating compressors and 14 screw compressors. These compressors are chosen from a drop-down menu containing 31 options including “None”.

Figure 8: Compressor specification

It is possible to include an open economizer for some of the screw compressors. When choosing a compressor, it is shown whether or not the model supports economizer, if so the economizer is chosen in the corresponding drop down menu. Additionally, each compressor can be operated with or without frequency control as indicated by the checkbox situated below the compressor specification.

Figure 9: Frequency control and economizer

It is not possible to simulate refrigeration plants including closed economizers for the screw compressors.

# Warm water production

The model enables four different methods of heat recovery for the refrigeration plant, chosen in the “Warm water production” menu.

Figure 10: Menu for specifying heat recovery configuration

In the following sections each of the methods are illustrated. The relevant input parameters for each method in Figure 10 are indicated by colors in the drawings and explained where needed.

Method One

In the first method heat is recovered by/through the desuperheater, condenser and oil coolers combined with the screw compressors.

Figure 11: Heat recovery by Method One

In the simulation interface this figure can be viewed by pressing “Model…” in the “Help” menu. The plant layouts of all methods are depicted in the help-file.

TC denotes the condensing temperature and T10 is the oil temperature at the compressor inlet previously mentioned in “5 General compressor settings”. The definitions of parameters not shown are as follows:

- HX temperature diff. (cold side), [C]:  T3-T1

- Condenser temperature diff. (hot side), [C]:  TC-T4

- Superheat at condenser inlet, [C]: T5-TC

The pump efficiency is common for both pumps shown in Figure 11. The boiling temperature and specific heat of water/glycol-mixture shown are valid for 40% water and 60% glycol. The pressure loss is valid for all heat exchanger passes marked with green.

The screw compressors are equipped with separate oil coolers as displayed in Figure 12. This is reflected in the model, as the user may specify the UA-values of these.

Figure 12: Oil coolers

Specifying the UA-value for reciprocating compressor will not be taken into account due to the fact that heat from these is not recovered. The oil inlet temperature (Figure 6) in the screw compressors also heavily impacts the heat recovery from the oil coolers.

The options concerning the heat pump do not influence the method of heat recovery.

Method Two

This method implements heat recovery similar to Method One, except regarding oil cooling the screw compressors. Hence, the oil cooling parameters do not influence the magnitude of heat recovery using this method.

Figure 13: Heat recovery without oil cooling

The relevant parameters are as defined in Method One.

Method Three

Here a heat pump, as well as oil cooling, is used in the heat recovery system.

Figure 14: Heat recovery with heat pump and no oil cooling

The parameters not shown in the figure are:

- Condenser temperature diff. (hot side), [C]:  TC - T6 and T7 - T4

- Temperature rise of heat pump, [K]: T7 - T6

T6 and T7 denote the evaporating and condensing temperatures of the heat pump circuit, respectively.

The capacity of the heat pump is to be specified. The heat pump power consumption is calculated using COPhp defined by

COPhp=Condensing heatPower

If the checkbox “Use standard heat pump” is marked, the model uses the following COPhp at full load

Figure 15: Standard heat pump COPhp at full load

This curve is found to be valid for HPO 24 from York Refrigeration. If the checkbox is left unmarked, the user-defined value is used. To find the pressure ratio as function of T7 and T6, help can be found in Table 5 placed at the end of the manual. In both cases the COPhp at part-load is calculated from the following relation

Figure 16: COPhp at part-load related to full-load

The polytropic coefficient of the heat pump circuit should also be specified by the user, and is then kept constant during simulations.

Method 4

The last method also includes a heat pump, but without heat recovery from oil coolers.

Figure 17: Heat recovery method with heat pump and without oil cooling

The parameters to be listed are the same as for the previous method.

# Cooling demands

An important feature in the model is the possibility of specifying varying cooling demands at each cooling stage. User defined cooling profiles created in the Profile Editor contained in the WinDali package achieves this.

## Profile Editor

This section is primarily based on the WinDali Manual included with the program.

As the Profile Editor application is executed the following window appears:

Figure 18: The Profile Editor window

First the duration of the profile is to be selected. The model is only able to handle profiles on a daily basis or less. If the profile interval is shorter than a day, it will be looping during the simulation. Then specify the interval of data provided to the profile. Now a table is created for entering values for the cooling profile. These values must be in percentage of the maximum cooling, which is to be specified in the Simulation Interface. The profile will automatically be updated in the plotting window.

Pressing <Save> saves the profile. An example of a profile is given in the figure below:

Figure 19: Example of cooling profile

The number of cooling profiles needed for the simulation should be saved under different names in the desired directory.

## Cooling demands

Handling of the saved cooling profiles in the simulation environment is done by  “Cooling demands”. This heading is pictured on the following figure.

Figure 20: Entering cooling profiles to the model

The model provides the opportunity to use up to 6 different profiles, two at each temperature level. The simulation period will be the specified number of days of period 1 and period 2 in the top of the menu. In this example the simulation period is one day for the profiles entered in period 1 only, thus period 2 and its profiles have no influence.

In the plot windows the loaded profiles can be viewed during simulation choosing  “Cooling Demands”.

# Graphs

A number of variables in the calculations can be graphed in the plot windows during the simulation. The chosen ones are those of most interest regarding heat recovery and include:

- Mass flow of process water, [kg/s]

- Temperature of process water, [C]

- Rate of heat recovery, [kW]

- Rate of heat recovery in condenser, [kW]

- Rate of heat recovery in desuperheater, [kW]

- Rate of heat recovery in oilcoolers, [kW]

- Cooling demands at all levels, [kW]

- Delivered cooling at all levels, [kW]

An example is given below.

Figure 21: Requested and delivered cooling

The graph expresses that the demand for cooling in the low stage is higher than what can be delivered during the middle hours of the day.

The variables are visualized activating checkboxes displayed in the “curve window” mentioned earlier. It should be noted that some (dynamic) variables of less interest are displayed in this window as well. To distinguish these values from the rest, each one is preceded with a “z” which puts them at the end of the list when sorting.

# Results

When a simulation is finished, activate this heading to display the results.

Figure 22: Results of simulation

A description for each value is given below.

The first section displays general information and settings. Each time simulation is run, the results are displayed as shown above. The first line in the window “Simulation number” keeps track of the number of conducted simulations. The indented lines display some general settings and useful information to distinguish one simulation from another. It is possible to save the results from each simulation in a text file by pressing the “save” button.

Deficit of cooling

The first three numbers sum up whether the cooling plant has been able to deliver the cooling demands during the simulation period or not. If not, the total deficit is shown in kWh.

Total power consumption in compressors

The values shown are the power consumption in compressors for each temperature level in kWh. In Figure 22 only the medium temperature level was included, thus only these compressors consumed electricity.

Hot water production

The total amount of hot water produced in m3 for the entire simulation period.

Heating of water from ordinary supply

This parameter expresses the demand for additional heating by other means than the heat recovery system in order to obtain the needed process water temperature. For the conducted simulation, the delivered water temperature is shown below

(1)

Figure 23: Delivered water temperature

Here the “T2, Needed temperature, [˚C]:” in the user interface is set to 65C, which cannot be sustained by the heat recovery system during the entire simulation. Therefore “Heating of water from ordinary supply” sums up to 20kWh, see Figure 22. It should be noted that the time with T14 = 0˚C, marked with (1), does not contribute to this, as there is no mass flow of process water.

Power consumption in heat recovery system

The total amount of power used in the heat recovery system [kWh]. This includes the power input to the pumps and the heat pump if applicable.

Savings

Total saving due to heat recovery. This result shows the financial value of the heat recovery, not including the price for electricity in the heat recovery system.

Heat Recovery

Shows the recovered amount of heat during one simulation.

Time with lack of evaporative condenser capacity

During the simulations the time with lack of evaporative condenser capacity is summed up, and the final value is displayed here.

Max heat pump capacity

Shown here is the maximum need for heat pump capacity during the simulation. This result is valid only for method 3 and 4. In the figure below the capacity of the heat pump is displayed. It is noted that the maximum value is depicted as the condensing capacity.  The maximum need for heat pump capacity would in this case be 108kW.

Figure 24: Heat pump capacity

Needed heat pump capacity (all compressors full load)

Only compressors chosen at active temperature levels (this case medium level) are included. Method 3 and 4 only.

Pressure ratio for heat pump

Method 3 and 4 only.

Max circulation pump capacity (all compressors full load)

The needed circulation pump (water/glycol) capacity when all compressors in the system operate at full capacity.

Max process water pump capacity (all compressors full load)

The needed process water pump capacity when all compressors in the system operate at full capacity.

# Parameter Analysis

The influence of changing parameters can be analyzed in two different ways described in this chapter.

## Varying parameters

By pressing <Vary> in the heading Cases, see Figure 3, one or more of the parameters can automatically be changed between simulations. This makes it possible to easily perform parameter studies in the model. If the model has a parameter called Volume and you want to vary it from 0.001 to 0.005 with a step of 0.001, the simulation will automatically run 5 times with the varying stepvalue.

Figure 25: Dialog for varying parameters

The results from the simulations are saved to one or more files. Which dependent variable will be saved is selected in the right panel. It is possible to vary more than one parameter. If it’s selected to vary Cold temperature (equal to ambient temperature in this particular model) from 20 to 25 with step 1 in addition to Volume as shown, this will result in 30 cases and thereby 30 simulations are generated as listed below.

Table 4: Cases when varying volume and ambient temperature

By selecting OK the following information appears on the Cases page:

Figure 26: Summarize of parameter variation

To actually perform the parameter variation “Run cases” has to be checked before the simulations are conducted. As simulations start, specifications on how to save the data generated must be set:

Figure 27: Saving settings for parameter variation

For each of the specified dependent variables one or more files will be created. Also, for each dependent variable a unique identifier has to specified – in the dialog T has been assigned the identifier A. The file(s) created will hold the name(s) File_ID_CaseNum.dat like: File_A_1.dat, File_A_2.dat, File_A_3.dat, File_A_4.dat and File_A_5.dat.

The file types in which data can be stored are listed here.

Individual ASCII files

Data will be saved to individual ASCII files, one file for each case, and one file for each dependent variable. The files have the following structure:

Time1;Dep

Time2;Dep

…

TimeN;Dep

Here Dep is the dependent variable for that file, and ‘;’ represents the selected column separator. In the example given above 5 files would be created, and one of them would contain:

Time1;T_1

Time2;T_2

…

TimeN;T_N

One merged ASCII file

Data for the different cases will be saved to one merged ASCII file for each dependent variable. One file has the following structure:

Time1;InDep1;InDep2;…InDepM;Dep_case1

Time2;…

…

TimeN;…

Time1;InDep1;InDep2;…InDepM;Dep_case2

…

…

TimeN;InDep1;InDep2;…InDepM;Dep_caseL

Where InDep1…InDepM are the independent variables (i.e. the parameters that are varied). In the example above the file would contain:

Time1;0.001;T_1

Time2;0.001;T_2

…

TimeN;0.001;T_N

Time1;0.002;T_1

…

…

TimeN;0.005;T_N

If Cold temperature were also varied, the file would contain:

Time1;0.001;20;T_1

Time2;0.001;20;T_2

…

TimeN;0.001;20;T_N

Time1;0.002;20;T_1

…

…

TimeN;0.005;20;T_N

Time1;0.001;21;T_1

…

…

…

TimeN;0.005;25;T_N

Individual binary files

Data is organized exactly as for individual ASCII files, except that the binary files do not contain line breaks or column separators.

One merged binary file

Data is organized exactly as for one merged ASCII file except that the binary files do not contain line shifts or column separators. Binary files can be saved in Double or in Single format. Each value in the file takes up 8 bytes of space in Double format, while each value in the file takes up 4 bytes of space in Single format. Although Single format saves space, it also has fewer significant digits.

By selecting OK in the dialog the user is asked to specify a directory in which the data is saved. At the end of the simulations an information file called CaseInfo.txt is written to this directory. It contains information about the created data files.

## Online Parameters

Changes in parameters while the simulation is running will not affect the calculations (at least not until the simulation is restarted). Experimenting with parameter changes while the simulation is running is done through the Online Parameters window.

In order to change parameters online, they have to be selected in the Online Parameters window before the simulation is carried out by pressing <Add online parameters>. Before or during the simulation the new values for the parameters are entered in the New column. Pressing <Update Parameters> will interchange the New and the Current columns. This helps to keep track of the old parameter values while new ones are entered for another interchange. Every time <Update Parameters> is pressed the changes will be recorded along with the time the changes were effected, and a vertical line will be drawn in the plots. The log can be printed together with plots and settings by selecting File|Print report or they can be printed/saved directly from the Log tab in the Online Parameters window.

Pressure ratio table

- The temperature, T6, is to be found in the header row.  T7 is to be found in the left column.

- The corresponding pressure ratio is read from the table. This curve for Max COP can be found on the next page. This curve is valid for HPO 24 from York Refrigeration and used as default.

| T6 T7 k | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 20 | 1,4 | 1,3 | 1,3 | 1,3 | 1,2 | 1,2 | 1,1 | 1,1 | 1,1 | 1,0 | 1,0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 22 | 1,5 | 1,4 | 1,4 | 1,3 | 1,3 | 1,3 | 1,2 | 1,2 | 1,1 | 1,1 | 1,1 | 1,0 | 1,0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 24 | 1,6 | 1,5 | 1,5 | 1,4 | 1,4 | 1,3 | 1,3 | 1,2 | 1,2 | 1,2 | 1,1 | 1,1 | 1,1 | 1,0 | 1,0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 26 | 1,7 | 1,6 | 1,6 | 1,5 | 1,5 | 1,4 | 1,4 | 1,3 | 1,3 | 1,2 | 1,2 | 1,2 | 1,1 | 1,1 | 1,1 | 1,0 | 1,0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 28 | 1,8 | 1,7 | 1,7 | 1,6 | 1,6 | 1,5 | 1,5 | 1,4 | 1,4 | 1,3 | 1,3 | 1,2 | 1,2 | 1,2 | 1,1 | 1,1 | 1,1 | 1,0 | 1,0 |  |  |  |  |  |  |  |  |  |  |  |  |
| 30 | 1,9 | 1,8 | 1,8 | 1,7 | 1,7 | 1,6 | 1,5 | 1,5 | 1,5 | 1,4 | 1,4 | 1,3 | 1,3 | 1,2 | 1,2 | 1,2 | 1,1 | 1,1 | 1,1 | 1,0 | 1,0 |  |  |  |  |  |  |  |  |  |  |
| 32 | 2,0 | 1,9 | 1,9 | 1,8 | 1,8 | 1,7 | 1,6 | 1,6 | 1,5 | 1,5 | 1,4 | 1,4 | 1,4 | 1,3 | 1,3 | 1,2 | 1,2 | 1,2 | 1,1 | 1,1 | 1,1 | 1,0 | 1,0 |  |  |  |  |  |  |  |  |
| 34 | 2,1 | 2,1 | 2,0 | 1,9 | 1,9 | 1,8 | 1,7 | 1,7 | 1,6 | 1,6 | 1,5 | 1,5 | 1,4 | 1,4 | 1,3 | 1,3 | 1,3 | 1,2 | 1,2 | 1,2 | 1,1 | 1,1 | 1,1 | 1,0 | 1,0 |  |  |  |  |  |  |
| 36 | 2,3 | 2,2 | 2,1 | 2,0 | 2,0 | 1,9 | 1,8 | 1,8 | 1,7 | 1,7 | 1,6 | 1,6 | 1,5 | 1,5 | 1,4 | 1,4 | 1,3 | 1,3 | 1,3 | 1,2 | 1,2 | 1,2 | 1,1 | 1,1 | 1,1 | 1,0 | 1,0 |  |  |  |  |
| 38 | 2,4 | 2,3 | 2,2 | 2,2 | 2,1 | 2,0 | 2,0 | 1,9 | 1,8 | 1,8 | 1,7 | 1,7 | 1,6 | 1,6 | 1,5 | 1,5 | 1,4 | 1,4 | 1,3 | 1,3 | 1,3 | 1,2 | 1,2 | 1,2 | 1,1 | 1,1 | 1,1 | 1,0 | 1,0 |  |  |
| 40 | 2,5 | 2,4 | 2,4 | 2,3 | 2,2 | 2,1 | 2,1 | 2,0 | 1,9 | 1,9 | 1,8 | 1,8 | 1,7 | 1,6 | 1,6 | 1,6 | 1,5 | 1,5 | 1,4 | 1,4 | 1,3 | 1,3 | 1,3 | 1,2 | 1,2 | 1,2 | 1,1 | 1,1 | 1,1 | 1,0 | 1,0 |
| 42 | 2,7 | 2,6 | 2,5 | 2,4 | 2,3 | 2,3 | 2,2 | 2,1 | 2,0 | 2,0 | 1,9 | 1,9 | 1,8 | 1,7 | 1,7 | 1,6 | 1,6 | 1,5 | 1,5 | 1,5 | 1,4 | 1,4 | 1,3 | 1,3 | 1,3 | 1,2 | 1,2 | 1,1 | 1,1 | 1,1 | 1,1 |
| 44 | 2,8 | 2,7 | 2,6 | 2,5 | 2,5 | 2,4 | 2,3 | 2,2 | 2,2 | 2,1 | 2,0 | 2,0 | 1,9 | 1,8 | 1,8 | 1,7 | 1,7 | 1,6 | 1,6 | 1,5 | 1,5 | 1,4 | 1,4 | 1,4 | 1,3 | 1,3 | 1,2 | 1,2 | 1,2 | 1,1 | 1,1 |
| 46 | 3,0 | 2,9 | 2,8 | 2,7 | 2,6 | 2,5 | 2,4 | 2,4 | 2,3 | 2,2 | 2,1 | 2,1 | 2,0 | 1,9 | 1,9 | 1,8 | 1,8 | 1,7 | 1,7 | 1,6 | 1,6 | 1,5 | 1,5 | 1,4 | 1,4 | 1,4 | 1,3 | 1,3 | 1,2 | 1,2 | 1,2 |
| 48 | 3,1 | 3,0 | 2,9 | 2,8 | 2,7 | 2,6 | 2,6 | 2,5 | 2,4 | 2,3 | 2,3 | 2,2 | 2,1 | 2,0 | 2,0 | 1,9 | 1,9 | 1,8 | 1,8 | 1,7 | 1,7 | 1,6 | 1,6 | 1,5 | 1,5 | 1,4 | 1,4 | 1,3 | 1,3 | 1,3 | 1,2 |
| 50 | 3,3 | 3,2 | 3,1 | 3,0 | 2,9 | 2,8 | 2,7 | 2,6 | 2,5 | 2,4 | 2,4 | 2,3 | 2,2 | 2,2 | 2,1 | 2,0 | 2,0 | 1,9 | 1,8 | 1,8 | 1,7 | 1,7 | 1,6 | 1,6 | 1,5 | 1,5 | 1,5 | 1,4 | 1,4 | 1,3 | 1,3 |
| 52 | 3,5 | 3,4 | 3,3 | 3,1 | 3,0 | 2,9 | 2,8 | 2,8 | 2,7 | 2,6 | 2,5 | 2,4 | 2,3 | 2,3 | 2,2 | 2,1 | 2,1 | 2,0 | 1,9 | 1,9 | 1,8 | 1,8 | 1,7 | 1,7 | 1,6 | 1,6 | 1,5 | 1,5 | 1,5 | 1,4 | 1,4 |
| 54 | 3,7 | 3,5 | 3,4 | 3,3 | 3,2 | 3,1 | 3,0 | 2,9 | 2,8 | 2,7 | 2,6 | 2,5 | 2,5 | 2,4 | 2,3 | 2,2 | 2,2 | 2,1 | 2,0 | 2,0 | 1,9 | 1,9 | 1,8 | 1,8 | 1,7 | 1,7 | 1,6 | 1,6 | 1,5 | 1,5 | 1,4 |
| 56 | 3,9 | 3,7 | 3,6 | 3,5 | 3,4 | 3,3 | 3,1 | 3,0 | 2,9 | 2,9 | 2,8 | 2,7 | 2,6 | 2,5 | 2,4 | 2,4 | 2,3 | 2,2 | 2,2 | 2,1 | 2,0 | 2,0 | 1,9 | 1,9 | 1,8 | 1,8 | 1,7 | 1,7 | 1,6 | 1,6 | 1,5 |
| 58 | 4,0 | 3,9 | 3,8 | 3,7 | 3,5 | 3,4 | 3,3 | 3,2 | 3,1 | 3,0 | 2,9 | 2,8 | 2,7 | 2,6 | 2,6 | 2,5 | 2,4 | 2,3 | 2,3 | 2,2 | 2,1 | 2,1 | 2,0 | 2,0 | 1,9 | 1,8 | 1,8 | 1,7 | 1,7 | 1,6 | 1,6 |
| 60 | 4,3 | 4,1 | 4,0 | 3,8 | 3,7 | 3,6 | 3,5 | 3,4 | 3,3 | 3,1 | 3,0 | 3,0 | 2,9 | 2,8 | 2,7 | 2,6 | 2,5 | 2,5 | 2,4 | 2,3 | 2,2 | 2,2 | 2,1 | 2,1 | 2,0 | 1,9 | 1,9 | 1,8 | 1,8 | 1,7 | 1,7 |
| 62 | 4,5 | 4,3 | 4,2 | 4,0 | 3,9 | 3,8 | 3,6 | 3,5 | 3,4 | 3,3 | 3,2 | 3,1 | 3,0 | 2,9 | 2,8 | 2,7 | 2,7 | 2,6 | 2,5 | 2,4 | 2,4 | 2,3 | 2,2 | 2,2 | 2,1 | 2,0 | 2,0 | 1,9 | 1,9 | 1,8 | 1,8 |
| 64 | 4,7 | 4,5 | 4,4 | 4,2 | 4,1 | 4,0 | 3,8 | 3,7 | 3,6 | 3,5 | 3,4 | 3,3 | 3,2 | 3,1 | 3,0 | 2,9 | 2,8 | 2,7 | 2,6 | 2,5 | 2,5 | 2,4 | 2,3 | 2,3 | 2,2 | 2,1 | 2,1 | 2,0 | 2,0 | 1,9 | 1,9 |
| 66 | 4,9 | 4,7 | 4,6 | 4,4 | 4,3 | 4,1 | 4,0 | 3,9 | 3,8 | 3,6 | 3,5 | 3,4 | 3,3 | 3,2 | 3,1 | 3,0 | 2,9 | 2,8 | 2,7 | 2,7 | 2,6 | 2,5 | 2,4 | 2,4 | 2,3 | 2,2 | 2,2 | 2,1 | 2,1 | 2,0 | 1,9 |

Table 5: Pressure ratio as funtion of T7 and T6

COPHP curve

COPHP at maximum capacity for HPO 24 from York Refrigeration.

COPHP

Pressure ratio